### FIRE                                               NORMAL OPERATING PROCEDURE

### (NOP)

ST JOSEPH’S CATHEDRAL PRIMARY SCHOOL

July 2021

##### TABLE OF CONTENTS

| SECTION 1 Workplace Details | Page 3 | SECTION 7 6 Monthly Duties | Page 10 |
| --- | --- | --- | --- |
| SECTION 2 Organisation and Responsibility | 5 | SECTION 8 Yearly Duties | 11 |
| SECTION 3 Fire Safety Appointments and Training | 6 | SECTION 9 Staff Training Programme | 12 |
| SECTION 4 Daily Duties | 7 | SECTION 10 Restricted Areas | 13 |
| SECTION 5 Weekly Duties | 8 | SECTION 11 Fire Records Contents | 14 |
| SECTION 6 Monthly Duties | 9 | APPENDIX 1 Inspection Details | 15 |

###### SECTION 1

Workplace Details

St Joseph’s Cathedral Primary School

Key Holders:

PSM

Angela Heald –HT

Caretaker

The Diocese of Menevia owns the school premises with the Directorate of the Education department being the landlord and the school acting as the tenant.

The Diocese of Menevia owns St Joseph’s Cathedral Primary School building.

St Joseph’s Cathedral Primary School consists of a four-storey main building and three storey annexe building. The school also has the use of the Parish Hall of St Joseph’s Cathedral. The school is owned by the Diocese of Menevia. The Headteacher is the Premises Manager and responsible for fire safety for the buildings.

The school is open between the hours of approximately 7.30 am and 6.00 pm Monday to Friday during term-time (39 weeks per year). The school runs a breakfast club from 8.00 am.  School events generally take place during the school day / daylight hours.  An After School Club, run by the school, operates daily from 3.25 pm – 5.15 pm.  The school is open ad hoc during school holiday periods.

There are robust management systems in place for all visitors and contractors. Any works that are being undertaken must be authorised by the head teacher or the deputy in their absence.

All staff have a duty to ensure Fire procedures are adhered to.

###### SECTION 2

Organisation and Responsibility for Fire Safety - Normal Operating Procedures

The Headteacher (HT) is the responsible person in relation to Fire Safety and must ensure that pertinent recommendations addressed in the risk assessment will be supported by written normal operating procedures NOP.

The HT may appoint a member of staff to assist with Fire Safety duties. The HT will ensure that sufficient time and resource is allotted to under take this role (if so required).

At St Joseph’s Cathedral Primary School the appointed member of staff is the caretaker.

The HT will ensure arrangements and duties (identified in this NOP) of the appointed will be fully co-ordinated.

The administration manager alongside the HT keeps the fire safety measures and equipment in the work place in effective working order.  This involves a commitment to:

Inspections

- Fire doors and self-closing devices

- Corridors, routes, classrooms and outside paths

- Firefighting equipment

- Notices and signage.

Testing

- Fire alarm system and break glass call points

- Emergency Lighting

Reporting

- Defects and concerns to the Development officer

Controlling

- Logging competent person inspection, tests and maintenance of equipment pertinent to the site Fire safety

Controlling

- Activities within their area of responsibility

Communications

- Ensure sufficient information has been passed on or is available to education staff and students on Fire Safety

Safety Contact Details

Corporate Health, Safety and Wellbeing Service – City & County of Swansea

01792 636210

###### SECTION 3

Workplace Precautions

- Fire NOP.

- Fire EAP.

- Supply of information to education staff & students.

- Display Fire Action Notices.

- Ensure escape routes are clear.

- Waste will be stored safely and collected at appropriate intervals.

- Maintain the appropriate portable firefighting equipment.

- Maintain fire safety signage to recommended standards.

- Undertake inspections, test, checks and drills as specified.

- Ensure fire growth and smoke spread potential is minimised by appropriate maintenance and procedures.

Fire Safety Appointments and Training

The Headteacher will:

- Ensure sufficient cover is available in cases of absenteeism, with designated responsibilities.

- Supply information to education staff in their duties with regard to normal fire duties and emergency duties.

- Instruct pupils, visitors and contractors on relevant fire safety procedures and ensure they have a designated contact in case of query.

SECTION 4

DAILY DUTIES

Duties are delegated by the Head Teacher:

- Caretaker

- Undertake a visual inspection of fire escape routes internally and externally to ensure all are free from obstruction.

- Record findings on above duties and report negative findings to appropriate person for remedial action to be initiated i.e. LA Facilities Management Department

- Ensure fire extinguishers are not obstructed.

- Ensure fire doors are kept closed and not wedged open.

- Be observant to members of the public; pupils or education staff who may be disabled to ensure that you can co-ordinate any help they require to escape during an emergency.

- Ensure facility telephone is operational.

- Ensure all colleagues, students, contractors or members of the public behave in an appropriate manner as not to endanger themselves or others.

- Ensure all combustibles are 1m from all sources of ignition.

- Ensure all paper and card is not stacked closer than 0.5m from light fittings.

- Return equipment to the dedicated store.

- Ensure all waste material is disposed of correctly and safely.

- All electrical equipment to be isolated at the end of every day (if safe to do so).

- Ensure all windows and doors are closed and secure at the end of every day.

- Classroom teachers/ teaching assistants

- To undertake a visual inspection of the classroom and the environment to ensure that all emergency exits are clear of any obstruction.

- Ensure that all fire extinguishers within the classrooms are visible and located in the correct location – report any issues to the HT or caretaker.

- All corridors and walkways are clear of any trip hazards.

###### SECTION 5

WEEKLY DUTIES / COMMITMENTS

Duties are delegated by the Head Teacher:

- Caretaker

- Ensure the fire alarm system and Break Glass call points are tested weekly at a pre-determined time using a different call point for each successive test to check that the sounders operate satisfactorily throughout the ground floor.  All call points must be tested within a 3month period.

- Keep suitable records of such testing of within the fire log book.

SECTION 6

MONTHLY DUTIES

Duties are delegated by the Head Teacher:

- Caretaker

- Visually inspect fire extinguishers on site and record finding.  The inspection should indicate that the extinguisher is in correct location, the safety pin is secured and check for any dents, corrosion, or damage that may impair the safe operation.  Particular attention should be paid to determining that the extinguisher has not been operated.  (If in doubt, report to LA Facilities Management Department / supplier for appropriate test and re-charge).  Record findings and ensure they are easily accessible.

- Ensure emergency lighting system is checked for condition and working order (record findings and ensure they are easily accessible).

- Ensure emergency exit doors, fire door self closing devices are inspected opened and re-secured and ensure finding are recorded.  Instigate repairs if required.

See Appendix 1 for inspection details.

SECTION 7

NEW TERM  DUTIES

Duties are delegated by the Head Teacher:

- Caretaker/ Head Teacher

- Ensure a fire drill exercise is undertaken to ensure that education staff and students are fully trained in fire safety procedures (Breakfast Club and After School club drills to be included).

- Conduct de-brief sessions or meetings on findings associated with fire safety or practice fire drills.

- Record details of fire drill (date, time, staff numbers etc) and place within section 7 of the Fire Management File.

SECTION 8

YEARLY DUTIES

- Head Teacher/Caretaker/ GB

- Undertake a review of current Fire Risk Assessment, NOP and EAP documentation and arrangements to ensure accuracy.

- Ensure that all documentation associated with fire safety has been compiled, recorded and stored.  (Inspections, tests and or maintenance logs / records).

- Ensure that the electrical supply and the portable and transportable electrical equipment comply with the City & County of Swansea Policy for Electrical Equipment and Installations.

- Ensure gas installation is checked by a competent registered fitter meeting the requirements of the supplier / manufacturers and the Council of Registered Gas Installers (CORGI) eg Corporate Property under the schools SLA

- Ensure the alarm system is checked and maintained by a competent person in line with current edition of BS 5839-Part1 (Fire Detection and Fire Alarm System for Buildings) and manufacturers / installers requirements. Ensure Emergency Lighting systems are maintained to appropriate standards (BS 5266-Part 1, Emergency Lighting) eg Corporate Property under the schools SLA

- Ensure that fire extinguishers are maintained to appropriate standards (BS 5306-Part 3 Fire Extinguishing Installations and Equipment on Premises).

WHEN NECESSARY

- HT & CHSWS,FM & Governor sub-committee

- Lead an investigation into any fire event and draft report.

- Ensure provision of suitable arrangements with regard to safety of contractors, events and visits.  (Ascertain if any “hot work” is to be carried out at your facility (welding / plumbing / open flame work) and contact the Corporate Health and Safety Section for guidance well in advance of such work.  (See EAP for contact details).

- Request a ‘Fire Method Statement’ from contractors who work on site.

SECTION 9

TRAINING PROGRAMME

- Familiarisation with the means of escape from the premises including all staff.

- Appreciation of the importance of fire resisting doors and of the need to close all doors at the time of a fire and on hearing the fire alarm.

- The method of calling the Fire Brigade.

- The location and familiarisation with fire fighting extinguishers.

- The action to be taken on discovering a fire.

- The action to be taken when the fire alarm sounds.

- Evacuation of the building

- The location of the assembly point.

- How to minimise the possibility of fire starting.

- The testing and Inspection procedures

SECTION 10

RESTRICTED AREAS

Areas of authorised access only to trained staff and approved contractors / visitors.

- Offices

- HT Room

- Store rooms

- Electrical Switch Gear Room

- Gas supply room

- Boiler Plant Room

- Corridor Cupboards

- Staff Room / First Aid Room

SECTION 11

FIRE LOG RECORDS (to include)

- Fire Drills (Twice a year minimum)

- Date.

- Time.

- Attendees groups (employees / visitors / disabled / young / old).

- Numbers.

- Evacuation times.

- Fire Alarm System (Weekly – in house)

- Type.

- Date of installation.

- General power supply and battery back-up performance information.

- System inspection (system fault and repair information)

- System Service and Test.

- System Maintenance or Repair.

- Fire Fighting Equipment (Monthly – in house)

- Inspection (fault information)

- Test / Service / Maintenance.

- Service Provider Information.

- Emergency Lighting (Monthly – in house)

- Date of Installation.

- Battery Performance.

- Inspection / Test (fault information and repair date).

- Service / Maintenance.

- Detectors (as per contract – at least annually)

- Service and Test

APPENDIX 1

CHECKS / INSPECTIONS by Caretaker

Inspection of Fire Extinguishers

- Correct location

- The Safety Pin is in place

- Plastic “flag” Tie in place

- Pressure gauge reading for optimum condition (if applicable).

- Check cylinder (extinguisher body) for dents, corrosion or damage

- Check hose / horn for damage

Inspection of Emergency Lighting

- Inspect emergency lighting fire log for faults

- Test all Emergency torches for operation and correct location (if applicable)

- Check torch battery stock (if applicable)

- Use “fish test key” to test units function

- Clean units if required

- Complete fire log book.

Inspection and check of Emergency Exits

- Inspect signage to ensure conformity

- Inspect door surround

- Inspect door for dents, corrosion, distortion, weathering and or damage

- Opening or unlocking mechanism should be operated to establish effectiveness and readily operated with reasonable force and involve one movement.  (A push bar or panic bolt type mechanisms).

- Open the door fully to at least 90o

- Inspect hinges for defects

- Inspect door recess for defects

- Inspect door fit for fire and smoke spread effectiveness and ease of opening

- Ensure doors are not propped open (unless for short duration operational needs).

Inspection of Outside Gates

- As Emergency Exits

- Locks and keys should be tested

- Locks should be cleaned and lubricated

- Ensure Gates are not propped open (unless for short duration operational needs ensure full supervision during these occasions).

Inspection of internal fire doors (on an ongoing basis)

- Inspect signage to ensure conformity

- Inspect door surround

- Inspect door for dents, corrosion, distortion and or damage

- Opening/unlocking mechanism should be operated to establish effectiveness and readily operated with reasonable force and involve one movement.

- Open the door fully to at least 90o

- Inspect hinges for defects

- Inspect door recess for defects

- Ensure doors are not propped open (unless for operational needs)

- Ensure vision glass panels (where fitted) are clean and free of any items, which could obscure the view, not cracked or damaged.

Inspection of Routes

- Inspect signage to ensure good order

- Inspect ceiling, walls and floor for fire resistance integrity

- Ensure route is clear of obstructions, damage and hazards.